## Logsheet
CENTRAL POWER RESEARCH INSTITUTE - SHORT CIRCUIT LABORATORY, BENGALURU
LOG-SHEET FOR LOSS MEASUREMENT ON TRANSFORMER
Type your readings over the yellow {{placeholders}}. Blue cells are pre-filled by ATRG. Do not rename sheets' defined names. Station: Losses & Winding Resistance
Header
Test series no.
CPRI sample code
Customer / Manufacturer | M/s. A.P. Transformers, Chennai
Rating | 250 kVA, 11000/433 V, 3-phase
Serial no. | 1098
Date of test | 29-10-2025
Date of test (after STC) | 04-11-2025
Oil temperature (°C)
Unit: °C | Before STC | After STC
Top oil | 25.5 | 27
Bottom oil | 23.9 | 25.8
Winding temperature during resistance measurement (°C)
Unit: °C | Before STC | After STC
Winding temp. | 24.7 | 25.9
Resistance of HV winding (Ω)
Unit: Ω | 1U1V | 1V1W | 1W1U
Normal tap - Before STC | 3.9736 | 3.9558 | 3.969
Highest tap - Before STC | 4.2028 | 4.1822 | 4.1874
Lowest tap - Before STC | 3.5476 | 3.5398 | 3.5458
Normal tap - After STC | 3.989 | 3.9734 | 3.9844
Highest tap - After STC | 4.22 | 4.1988 | 4.2092
Lowest tap - After STC | 3.5612 | 3.554 | 3.5622
Resistance of LV winding (mΩ)
Unit: mΩ | 2u2v | 2v2w | 2w2u
Before STC | 3.8716 | 3.865 | 3.9074
After STC | 3.897 | 3.8844 | 3.9248
Measurement of no-load loss (raw readings)
Unit: V, A, W, Hz | V12 | V23 | V31 | I1 | I2 | I3 | W1 | W2 | W3 | Freq
BT | 251.133 | 252.816 | 246.166 | 1.907 | 1.645 | 1.714 | 109.18 | 84.52 | 189.22 | 49.95
AT | 250.158 | 252.721 | 246.869 | 1.893 | 1.638 | 1.73 | 104.53 | 88.28 | 190.69 | 49.99
112.5 % | 266.596 | 284.378 | 293.096 | 4.681 | 3.937 | 4.165 | 98.86 | 165.57 | 268.72 | 49.96
No-load loss results (rated voltage)
Unit: V, A, W, Hz | Voltage | Current (avg) | No-load loss | Frequency
Before STC | 433.05 | 1.689 | 383.18 | 49.95
After STC | 433.02 | 1.687 | 383.26 | 49.99
No-load current at 112.5 % voltage
Unit: V, A | Voltage | Current (avg)
112.5 % V | 487.32 | 4.261
Measurement of 50 % load loss
Unit: V, A, W, Hz | Voltage | Current | Watts | Freq
Before STC | 137.07 | 6.517 | 443.04 | 49.885
After STC | 138.24 | 6.553 | 448.2 | 49.968
Measurement of load loss (per tap)
Unit: V, A, W, Hz | V1 | V2 | V3 | I1 | I2 | I3 | P1 | P2 | P3 | Freq
Nor. BT | 267.85 | 268.49 | 263.62 | 12.706 | 12.718 | 12.576 | 568.91 | 565.64 | 542.57 | 49.886
Nor. AT | 273.45 | 273.81 | 269.6 | 12.936 | 12.935 | 12.819 | 588.76 | 586.96 | 568.04 | 49.959
Hig. BT | 273.45 | 273.66 | 269.03 | 11.607 | 11.588 | 11.48 | 508.05 | 508.62 | 490.73 | 49.876
Hig. AT | 270.67 | 271.09 | 266.12 | 11.452 | 11.449 | 11.342 | 498.22 | 493.92 | 482.26 | 49.944
Low. BT | 247.35 | 248.33 | 242.53 | 14.175 | 14.158 | 13.954 | 615.33 | 598.64 | 579.45 | 49.878
Low. AT | 242.61 | 244.44 | 238.47 | 13.866 | 13.869 | 13.672 | 590.73 | 577.67 | 557.86 | 49.955
Customer's Signature | [6 empty] | Test Engineer
DOCUMENT : FORMS & FORMATS - generated by CPRI ATRG

## Datasheet
CENTRAL POWER RESEARCH INSTITUTE - SHORT CIRCUIT LABORATORY, BENGALURU
DATASHEET FOR LOSSES CALCULATION (CPRI SCL Transformer Loss Measurement)
Type your readings over the yellow {{placeholders}}. Blue cells are pre-filled by ATRG. Do not rename sheets' defined names. Station: Losses & Winding Resistance
Load loss results (reference temperature 75 °C)
Unit: %, Ω, mΩ, W, kA | %Z-75°C | %X-50Hz | Rhv | Rlv | 100% load loss | X/R-75°C | Isc-pk | Isc-rms | Stray loss | 50% load loss | 50% total loss | 100% total loss | %X change
NorBT | 4.38 | 4.299 | 7.101 | 2.317 | 2102.74 | 5.112 | 16.73 | 7.61 | 107.62 | 524.91 | 908.09 | 2485.92
NorAT | 4.387 | 4.306 | 7.098 | 2.318 | 2101.21 |  |  |  | 106.21 | 523.61 | 906.87 | 2484.47 | -0.163
HigBT | 4.442 | 4.365 | 7.504 | 2.317 | 2056.03 | 5.31 | 16.61 | 7.5 | 111.77 |  |  | 2439.21
HigAT | 4.446 | 4.369 | 7.502 | 2.318 | 2054.67 |  |  |  | 110.09 |  |  | 2437.93 | -0.092
LowBT | 4.487 | 4.397 | 6.346 | 2.317 | 2240.03 | 4.907 | 16.2 | 7.43 | 118.6 |  |  | 2623.21
LowAT | 4.496 | 4.406 | 6.343 | 2.318 | 2239.94 |  |  |  | 118.58 |  |  | 2623.2 | -0.205
Customer's Signature | [6 empty] | Test Engineer
DOCUMENT : FORMS & FORMATS - generated by CPRI ATRG