## Logsheet
CENTRAL POWER RESEARCH INSTITUTE - SHORT CIRCUIT LABORATORY, BENGALURU
LOG SHEET FOR AIR PRESSURE TESTS AND OIL LEAKAGE TEST
Type your readings over the yellow {{placeholders}}. Blue cells are pre-filled by ATRG. Do not rename sheets' defined names. Station: Pressure & Oil Leakage
Header
Test series no.
CPRI sample code
Customer / Manufacturer | M/s. A.P. Transformers, Chennai
Rating | 250 kVA, 11000/433 V, 3-phase
Serial no. | 1098
Date of test | 14-11-2025
Ambient conditions
Atmospheric pressure (kPa) | 91
Ambient temperature (°C) | 25
Relative humidity (%) | 62
Pressure test - routine
Applied air pressure (kPa) | 35
Test duration (min) | 10
Remarks / observation | No leakage and no permanent deformation
Pressure test - type (air)
Applied air pressure (kPa) | 80
Test duration (min) | 30
Flat plate length (mm) | 700
Flat-plate deflection - air pressure (mm)
Unit: mm | Initial | Final
Point 1 | 259.99 | 259.64
Point 2 | 174.3 | 174.16
Point 3 | 181.35 | 181.13
Point 4 | 186.61 | 186.58
Point 5 | 276.99 | 275.91
Point 6 | 231.09 | 231.06
Pressure test - type (air) result
Permanent deflection after release of air pressure (mm) | 1.08
Observation | No permanent deformation beyond limit
Vacuum test - type
Vacuum applied (mmHg) | 760
Test duration (min) | 30
Flat-plate deflection - vacuum (mm)
Unit: mm | Initial | Final
Point 1 | 259.4 | 257.54
Point 2 | 174.19 | 173.45
Point 3 | 186.01 | 185.74
Point 4 | 174.93 | 174.79
Point 5 | 261.26 | 258.39
Point 6 | 232.96 | 232.69
Vacuum test - result
Permanent deflection after release of vacuum (mm) | 2.87
Observation | No permanent deformation beyond limit
Oil leakage test
Head pressure calculated at base of tank (kPa) | 14
Test pressure at base of tank (kPa) | 28
Test duration (h) | 8
Observation | No leakage at any point
Customer's Signature |  |  | Test Engineer
DOCUMENT : FORMS & FORMATS - generated by CPRI ATRG