## Logsheet
CENTRAL POWER RESEARCH INSTITUTE - SHORT CIRCUIT LABORATORY, BENGALURU
LOG-SHEET FOR SHORT CIRCUIT TEST ON TRANSFORMERS
Type your readings over the yellow {{placeholders}}. Blue cells are pre-filled by ATRG. Do not rename sheets' defined names. Station: Short-Circuit Withstand
Header
Test series no.
CPRI sample code
Customer / Manufacturer | M/s. A.P. Transformers, Chennai
Rating | 250 kVA, 11000/433 V, 3-phase
Serial no. | 1098
Date of test | 31-10-2025
Condition of transformer before SC test | As after routine test
Short-circuit current required on LV side
Unit: kA | kA rms | kA peak
Normal tap | 7.61 | 16.73
Highest tap | 7.5 | 16.61
Lowest tap | 7.43 | 16.2
S.C. test results (oscillograms)
Unit: kV, kA, s | Dial | kV U | kV V | kV W | Tap | Peak | RMS U | RMS V | RMS W | RMS avg | Duration | S.E.
S001 | 145 | 3.7 | 3.5 | 3.6 | NT | 5.32 | 2.07 | 2.11 | 2.07 | 2.08 | 0.54
S002 | 145 | 11.9 | 11.4 | 11.6 | NT | 16.8 | 7.45 | 7.59 | 7.53 | 7.53 | 0.54 | 8.2
S003 | 155 | 11.9 | 11.4 | 11.6 | NT | 16.82 | 7.57 | 7.76 | 7.65 | 7.66 | 0.54 | 8.4
S004 | 155 | 11.9 | 11.4 | 11.6 | NT | 16.74 | 7.61 | 7.85 | 7.68 | 7.71 | 0.54 | 8.4
S005 | 100 | 12.5 | 12.1 | 12.3 | HT | 16.89 | 7.48 | 7.45 | 7.62 | 7.52 | 0.54 | 8.6
S006 | 100 | 12.5 | 12.1 | 12.3 | HT | 16.78 | 7.53 | 7.46 | 7.64 | 7.54 | 0.54 | 8.6
S007 | 100 | 12.5 | 12.1 | 12.3 | HT | 16.72 | 7.51 | 7.44 | 7.65 | 7.53 | 0.54 | 8.6
S008 | 40 | 10.6 | 10.5 | 10.5 | LT | 16.49 | 7.68 | 7.56 | 7.64 | 7.63 | 0.54 | 7.8
S009 | 40 | 10.6 | 10.5 | 10.5 | LT | 16.34 | 7.47 | 7.4 | 7.44 | 7.44 | 0.54 | 7.6
S010 | 40 | 10.6 | 10.5 | 10.5 | LT | 16.26 | 7.5 | 7.39 | 7.47 | 7.45 | 0.54 | 7.6
S011 | 70 | 11.1 | 10.7 | 10.4 | NT |  | 7.53 | 7.58 | 7.55 | 7.55 | 2.01 | 8.4
Observations and physical inspection
Observation during test | No abnormalities
Observation after test | No abnormalities
Conductor, core & clampings | No visible damage
Spacers / support blocks | Intact
Oil | Clear
Customer's Signature | [6 empty] | Test Engineer
DOCUMENT : FORMS & FORMATS - generated by CPRI ATRG