## Request
CPRI - CUSTOMER REQUEST FORM (CPRI/QAF/01A) + PROFORMA FOR TRANSFORMERS
Type over the yellow {{placeholders}} and upload this file on the New Test Request page to auto-fill the form. Allowed values are listed in column D.
1. Customer & sample (Request form - sheet 1)
Name of the customer * | M/s. A.P. Transformers
Address of the customer * | SP24 & 95H/1(SP), Ambattur Indl. Estate, Chennai-600058
Sample(s) to be tested * | Three Phase Distribution Transformer
Rating * | 250 kVA, 11000 / 433 V
Description of test sample | 250 kVA, 11 kV / 433 V, 3-phase, oil-immersed, ONAN, outdoor distribution transformer
Type | Outdoor, Non-sealed, Oil immersed
Serial number(s) * | 1098
Manufacturer's name & address * | M/s. A.P. Transformers, SP24 & 95H/1(SP), Ambattur Indl. Estate, Chennai-600058
Customer's requirement | Nil
Criteria for evaluation (standard / specification) * | IS 1180 (Part 1): 2014 (with Amendment No.4: March 2021)
Number of samples * | 1
Sample storage / handling / disposal - take back the sample? | Yes | Yes / No
Details of test(s) requested | Type tests, all routine tests and special tests as per IS 1180 (Part 1): 2014
Specific mounting / connection instructions | Nil
Witnessing person - customer's representative | Mr. Vivekanand Krishna
Witnessing person - other than customer | None
Test report to be dispatched to | M/s. A.P. Transformers, Ambattur Indl. Estate, Chennai-600058
Mode of dispatch | Courier | By hand / Speed post / Courier / E-mail (scanned copy)
Number of additional reports required | 0
2. Request form - sheet 2
MSME discount applicable? | No | Yes / No
Statement of conformity required? | Yes | Yes / No
If yes, decision rule | (i) | (i) / (ii) / (iii)
3. Proforma for transformers (manufacturer-declared data)
Type - sealing | Non-sealed | Sealed / Non-sealed
Type - insulation | Oil immersed | Oil immersed / Dry type
Type - installation | Outdoor | Indoor / Outdoor
Rated power (kVA) * | 250
Rated voltage HV (V) * | 11000
Rated voltage LV (V) * | 433
Highest voltage for equipment Um (kV) | 12
HV insulation level LI (kVp) | 75
HV insulation level AC (kVrms) | 28
LV insulation level LI (kVp) | -
LV insulation level AC (kVrms) | 3
Impedance voltage at 75 °C (%) * | 4.50
Number of phases | 3 | 3 / 1
Rated frequency (Hz) | 50
Vector group * | Dyn11
Energy efficiency level | EEL-1 | EEL-1 / EEL-2 / EEL-3 / EEL-4 / EEL-5
Type of cooling | ONAN
Tapping range + (%) | 5
Tapping range - (%) | 10
Tap step (%) | 2.5
Number of taps | 7
Principal tap position | 3
Declared no-load loss (W) | 385
Declared load loss at 75 °C (W) | 2250
Maximum total loss at 50 % load (W) * | 980
Maximum total loss at 100 % load (W) * | 2930
Noise level (dB) | -
Volume of oil (litres) | 460
Month & year of manufacture (MM/YYYY) | 10/2025
Winding material | Copper | Copper / Aluminium
Coil shape | Circular | Circular / Non-circular
Core material | CRGO | CRGO / Amorphous
LV winding type | Helical / Spiral
HV winding type | Crossover
Tank construction | Plain | Plain / Corrugated
Guaranteed max. temperature rise - top oil (°C) | 35
Guaranteed max. temperature rise - winding (°C) | 40
Drawing numbers (one per row: number ¦ sheet no. ¦ revision)
APT/250-11/001 | 1 of 1 | 0
APT/250-11/001B | 1 of 1 | 0
{{req.drawing3_number}} | {{req.drawing3_sheet}} | {{req.drawing3_rev}}
{{req.drawing4_number}} | {{req.drawing4_sheet}} | {{req.drawing4_rev}}
{{req.drawing5_number}} | {{req.drawing5_sheet}} | {{req.drawing5_rev}}
Tests requested (type Yes / No)
Short-circuit withstand test (dynamic + thermal) [21.4 b)] | Yes
No-load current at 112.5 % voltage [21.4 c)] | Yes
Temperature-rise test [21.3 b)] | Yes
Pressure test [21.3 d)] | Yes
Measurement of winding resistance [21.2 a)] | Yes
Measurement of voltage ratio and check of phase displacement (vector group) [21.2 b)] | Yes
Measurement of short-circuit impedance and load loss [21.2 c)] | Yes
Measurement of no-load loss and current [21.2 d)] | Yes
Measurement of insulation resistance [21.2 e)] | Yes
Induced over-voltage withstand test [21.2 f)] | Yes
Separate source voltage withstand test [21.2 g)] | Yes
Pressure test (routine) [21.2 h)] | Yes
Oil leakage test [21.2 j)] | Yes