## Logsheet
CENTRAL POWER RESEARCH INSTITUTE - SHORT CIRCUIT LABORATORY, BENGALURU
LOG SHEET FOR ROUTINE TESTS ON TRANSFORMERS
Type your readings over the yellow {{placeholders}}. Blue cells are pre-filled by ATRG. Do not rename sheets' defined names. Station: Routine Tests
Header
Test series no. | CPRIBLRSCL25T1654
CPRI sample code | HVD25S0847
Customer / Manufacturer | M/s. A.P. Transformers, Chennai
Rating | 250 kVA, 11000/433 V, 3-phase
Serial no. | 1098
Date of test | 29-10-2025
Ambient conditions
Unit: °C, % | Ambient (°C) | RH (%)
BT | 26.8 | 59.8
AT | 24.7 | 71
Vector group
| BT | AT
Vector group | Dyn11 | Dyn11
Insulation resistance (GΩ)
Unit: GΩ | BT | AT
H.V. to Earth | 4.19 | 6.11
L.V. to Earth | 1.22 | 1.35
H.V. to L.V. | 6.36 | 7.81
Induced over-voltage test
Unit: V, A, Hz, s | BT | AT
Voltage | 866 | 866
Current | 1.58 | 1.66
Frequency | 100 | 100
Duration | 60 | 60
Observation | No disruptive discharge, withstood | No disruptive discharge, withstood
Separate source (power frequency) voltage withstand
Unit: kV, s, mA | BT | AT
H.V. Voltage | 28 | 28
H.V. Duration | 60 | 60
H.V. Current | 22 | 22
H.V. Observation | No disruptive discharge, withstood | No disruptive discharge, withstood
L.V. Voltage | 3 | 3
L.V. Duration | 60 | 60
L.V. Current | 64 | 64
L.V. Observation | No disruptive discharge, withstood | No disruptive discharge, withstood
Voltage ratio
| BT A(U) | BT B(V) | BT C(W) | AT A(U) | AT B(V) | AT C(W)
Tap 1 | 46.38 | 46.36 | 46.26 | 46.37 | 46.37 | 46.26
Tap 2 | 45.22 | 45.22 | 45.12 | 45.23 | 45.23 | 45.13
Tap 3 | 44.1 | 44.09 | 44.06 | 44.11 | 44.09 | 44.07
Tap 4 | 43.02 | 43.01 | 42.96 | 43.03 | 43.05 | 43
Tap 5 | 41.92 | 41.92 | 41.92 | 41.93 | 41.92 | 41.92
Tap 6 | 40.82 | 40.86 | 40.86 | 40.81 | 40.86 | 40.81
Tap 7 | 39.73 | 39.72 | 39.72 | 39.73 | 39.72 | 39.72
Customer's Signature | [6 empty] | Test Engineer
DOCUMENT : FORMS & FORMATS - generated by CPRI ATRG