TEST REPORT

| Test Report Number |  | : | CPRIBLRSCL25T1654 Date: 18-11-2025 |  |
| --- | --- | --- | --- | --- |
| Name and Address of the Customer |  | : | M/s. A.P. Transformers SP24 & 95H/1(SP), Ambattur Indl. Estate, Chennai-600058 |  |
| Name and Address of the Manufacturer |  | : | M/s. A.P. Transformers, SP24 & 95H/1(SP), Ambattur Indl. Estate, Chennai-600058 |  |
| Particulars of sample tested |  | : | 250 kVA, 11000 / 433 V, Three Phase Distribution Transformer |  |
| Type |  | : | Outdoor, Non-sealed, Oil immersed |  |
| Description of test sample |  | : | Refer Sheet 2 of 11 |  |
| Serial Number |  | : | 1098 |  |
| Number of samples tested |  | : | One |  |
| Date(s) of Test (s) |  | : | 29-10-2025 to 14-11-2025 |  |
| CPRI Sample Code Number (s) |  | : | HVD25S0847 |  |
| Particulars of tests conducted |  | : | Type Tests, All Routine Tests & Special Tests (Refer Sheet 3 of 11) |  |
| Test in accordance with Standard / specification |  | : | IS 1180 (Part 1): 2014 (with Amendment No.4: March 2021) |  |
| Sampling plan |  | : | Not applicable |  |
| Customer’s requirement |  | : | Nil |  |
| Deviations if any |  | : | Nil |  |
| Name of the witnessing persons |  |  |  |  |
| Customer’s representative |  | : | Mr. Vivekanand Krishna |  |
| Other than customer’s representative |  | : | None |  |
| Test subcontracted with address of the laboratory |  | : | None |  |
| Documents constituting this Report (In words) |  |  |  |  |
| Number of Sheet(s) |  | : | Eleven (11) |  |
| Number of Oscillogram (s) |  | : | Ten |  |
| Number of Graph (s) |  | : | Two |  |
| Number of Photograph(s) |  | : | Four |  |
| Number of Test Circuit Diagram(s) |  | : | One |  |
| Number of Drawing(s) |  | : | Two |  |
| P. Naveenkumar Test Engineer |  |  |  | HOD (dry run) Reviewed and Authorized by |

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

DESCRIPTION OF SAMPLE TESTED

(As assigned by the manufacturer)

| Test sample |  | : | Three Phase Distribution Transformer |
| --- | --- | --- | --- |
| Type |  | : | Outdoor, Non-sealed, Oil immersed |
| Serial number |  | : | 1098 |
| Rated power |  | : | 250 kVA |
| Rated voltage – HV / LV |  | : | 11000 V / 433 V |
| Highest voltage of the equipment – Um |  | : | 12 kV |
| Insulation levels |  |  |  |
| HV LI / AC |  | : | 75 kVp / 28 kVrms |
| LV LI / AC |  | : | - / 3 kVrms |
| Impedance (Percent) |  | : | 4.50 % |
| Number of phases |  | : | Three |
| Rated frequency |  | : | 50 Hz |
| Vector group |  | : | Dyn11 |
| Tappings |  | : | +5 % to -10 % in steps of 2.5 % (7 positions), off-circuit |
| Energy efficiency |  | : | Energy Efficiency Level - 1 |
| Type of cooling |  | : | ONAN |
| Maximum total loss at 50% load |  | : | 980 W |
| Maximum total loss at 100% load |  | : | 2930 W |
| Coil |  | : | Copper, Circular |
| Core material |  | : | CRGO |
| Month & Year of Manufacture |  | : | October 2025 |
| Volume of oil |  | : | 460 litres |
| Winding details |  |  |  |
| L.V. winding |  | : | Type : Helical / Spiral Conductor : Copper |
| H.V. winding |  | : | Type : Crossover Conductor : Copper |
| P. Naveenkumar Test Engineer |  |  |  |

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

SUMMARY OF TESTS CONDUCTED

| 1. Tests conducted | : | Refer the below table |
| --- | --- | --- |
| 2. Rating for which tested | : | Refer Sheet 5 of 11 to Sheet 10 of 11 |
| 3. Schedule of tests |  |  |

The clause numbers of the standard IS 1180 (Part 1): 2014 (with Amendment No.4: March 2021) pertain to the test(s) conducted are detailed in the following table.

| Tests Conducted | Clause Number (s) | Sheet |
| --- | --- | --- |
| Special Tests |  |  |
| Short-circuit withstand test (Ability to withstand the Dynamic Effects of Short circuit and Thermal Ability to withstand Short Circuit) | 21.4 b) | 7 of 11 & 8 of 11 |
| No load current at 112.5 percent voltage | 21.4 c) | 10 of 11 |
| Type Tests |  |  |
| Temperature-rise test | 21.3 b) | 9 of 11 |
| Pressure test | 21.3 d) | 10 of 11 |
| All Routine Tests |  |  |
| Measurement of winding resistance | 21.2 a) | 5 of 11 |
| Measurement of voltage ratio and check of phase displacement | 21.2 b) | 5 of 11 |
| Measurement of short-circuit impedance and load loss at 50% and 100% load | 21.2 c) | 5 of 11 |
| Measurement of no-load loss and current | 21.2 d) | 5 of 11 |
| Measurement of insulation resistance | 21.2 e) | 6 of 11 |
| Induced over-voltage withstand test | 21.2 f) | 6 of 11 |
| Separate source voltage withstand test | 21.2 g) | 6 of 11 |
| Pressure test | 21.2 h) | 8 of 11 |
| Oil leakage test | 21.2 j) | 8 of 11 |

| 4. Oscillogram number(s) | : | CPRIBLRSCL25T1654S002, CPRIBLRSCL25T1654S003, CPRIBLRSCL25T1654S004, CPRIBLRSCL25T1654S005, CPRIBLRSCL25T1654S006, CPRIBLRSCL25T1654S007, CPRIBLRSCL25T1654S008, CPRIBLRSCL25T1654S009, CPRIBLRSCL25T1654S010 & CPRIBLRSCL25T1654S011 |
| --- | --- | --- |
| 5. Graph number(s) | : | CPRIBLRSCL25T1654G01 & CPRIBLRSCL25T1654G02 |
| 6. Photograph number(s) | : | CPRIBLRSCL25T1654P01, CPRIBLRSCL25T1654P02, CPRIBLRSCL25T1654P03 & CPRIBLRSCL25T1654P04 |
| 7. Test circuit diagram number(s) | : | CRTL/SC/TR-07B |
| 8. Drawing Numbers | : | Refer Sheet 4 of 11 |

(P. Naveenkumar)

Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

LIST OF DRAWINGS

Drawing Numbers

Manufacturer has guaranteed that the sample submitted for the test (s) has been manufactured in accordance with the following drawings.

| Sl. No. | Drawing Number | Sheet Number | Revision Number |
| --- | --- | --- | --- |
| 1 | APT/250-11/001 | 1 of 1 | 0 |
| 2 | APT/250-11/001B | 1 of 1 | 0 |

It is verified that these drawings adequately represent the sample tested. Verification of this drawing by CPRI is limited to dimensional check only wherever possible.

P. Naveenkumar Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

# TEST RESULTS

| ROUTINE TESTS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Measurement of winding resistance |  |  |  |  |  |  |
|  | # Before SCW test |  |  | # After SCW test |  |  |
| # Tap switch position | # Principal (3) | # Highest (1) | # Lowest (7) | # Principal (3) | # Highest (1) | # Lowest (7) |
| HV winding resistance at 75 ºC () # -average | # 4.7343 | # 5.0025 | # 4.2309 | # 4.7317 | # 5.0015 | # 4.2289 |
| LV winding resistance at 75 ºC (m) # -average | # 4.6331 |  |  | # 4.6364 |  |  |

| Measurement of voltage ratio |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| # Tap switch position | # Tapping % | # Before SCW test |  |  | # After SCW test |  |  |
|  |  | # U | # V | # W | # U | # V | # W |
| # 1 | # +5.0 | # 46.38 | # 46.36 | # 46.26 | # 46.37 | # 46.37 | # 46.26 |
| # 2 | # +2.5 | # 45.22 | # 45.22 | # 45.12 | # 45.23 | # 45.23 | # 45.13 |
| # 3 | # 0.0 | # 44.10 | # 44.09 | # 44.06 | # 44.11 | # 44.09 | # 44.07 |
| # 4 | # -2.5 | # 43.02 | # 43.01 | # 42.96 | # 43.03 | # 43.05 | # 43.00 |
| # 5 | # -5.0 | # 41.92 | # 41.92 | # 41.92 | # 41.93 | # 41.92 | # 41.92 |
| # 6 | # -7.5 | # 40.82 | # 40.86 | # 40.86 | # 40.81 | # 40.86 | # 40.81 |
| # 7 | # -10.0 | # 39.73 | # 39.72 | # 39.72 | # 39.73 | # 39.72 | # 39.72 |

Check of phase displacement

Vector group was found to be Dyn11

| Measurement of short circuit impedance and load loss at 50% and 100% load |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | # Before SCW test |  |  | # After SCW test |  |  |  |
| # Tap switch position | # Principal (3) | # Highest (1) | Lowest # (7) | # Principal (3) | # Highest (1) | Lowest # (7) |  |
| # % Impedance at 75 ºC | # 4.380 | # 4.442 | # 4.487 | # 4.387 | # 4.446 | # 4.496 |  |
| Load loss at 75 ºC (W) | # 2102.74 | # 2056.03 | # 2240.03 | # 2101.21 | # 2054.67 | # 2239.94 |  |
| Load loss at 50% of full load at 75 ºC (W) | # 524.91 | # --- | # --- | # 523.61 | # --- | # --- |  |

Measurement of no-load loss and current

| Condition of the sample | Voltage (V) | Frequency (Hz) | No-load current (A) | No-load loss(W) |
| --- | --- | --- | --- | --- |
| Before SCW test | 433.05 | 49.95 | 1.689 | 383.18 |
| After SCW test | 433.02 | 49.99 | 1.687 | 383.26 |

# SCW – Short-Circuit Withstand

P. Naveenkumar

Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

# TEST RESULTS

ROUTINE TESTS (Contd...)

Check of Energy Efficiency Level

|  | # Before SCW test | # After SCW test |
| --- | --- | --- |
| Total loss at 50% load (W) | 908.09 | 906.87 |
| Total loss at 100% load (W) | 2485.92 | 2484.47 |

Measurement of insulation resistance

| Insulation resistance of | Before SCW test | After SCW test |
| --- | --- | --- |
| HV winding with respect to LV winding & tank connected together and earthed. | 4.19 GΩ | 6.11 GΩ |
| LV winding with respect to HV winding & tank connected together and earthed. | 1.22 GΩ | 1.35 GΩ |
| HV winding with respect to LV winding with tank earthed. | 6.36 GΩ | 7.81 GΩ |

Induced over-voltage withstand test

| Test on | Before SCW test | After SCW test |
| --- | --- | --- |
| LV winding by keeping HV winding open circuit | 866 V, 100 Hz for 60 s Withstood | 866 V, 100 Hz for 60 s Withstood |

Separate source voltage withstand test

| Test on | Before SCW test | After SCW test |
| --- | --- | --- |
| a) HV winding and all terminals of LV winding & tank connected together to earth b) LV winding and all terminals of HV winding & tank connected together to earth | 28.0 kV for 60 s Withstood 3.0 kV for 60 s Withstood | 28.0 kV for 60 s Withstood 3.0 kV for 60 s Withstood |

SCW – Short-Circuit Withstand

P. Naveenkumar

Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

# TEST RESULTS

| # SPECIAL TEST |  |
| --- | --- |
| # SHORT-CIRCUIT WITHSTAND TEST |  |
| # Test conditions |  |
| # Source | # Short-circuit generator |
| # Phases | # Three |
| # Frequency | # 50 Hz |
| # Test sample |  |
| # Condition before test | # Transformer as after routine tests |
| # Mounting | # Transformer tank isolated and grounded through the protection current transformer |
| # Connection |  |
| # LV terminals | # Shorted |
| # HV terminals | # Connected to source |
| # Test details |  |
| # Test circuit drawing number | # CRTL/SC/TR-07B |
| # Short-circuit |  |
| # Type | # Pre-set |
| # Applied on | # LV terminals through non-inductive current measuring shunt |
| # Short-circuit point | # Grounded |

Short-circuit current calculation

| # Tap switch position | # X/R at 75 ºC | # Required short-circuit current on LV side (kA) |  |
| --- | --- | --- | --- |
|  |  | # rms | # peak |
| 3 (Principal) | # 5.112 | # 7.61 | # 16.73 |
| 1 (Highest) | # 5.310 | # 7.50 | # 16.61 |
| 7 (Lowest) | # 4.907 | # 7.43 | # 16.20 |

| Ability to Withstand the Dynamic Effects of Short-Circuit # [Sub-clause 4.2 of IS: 2026 (Part-5):2011] |  |  |  |  |
| --- | --- | --- | --- | --- |
| # Oscillogram number | Current # peak (kA) | Current rms (kA) # (Average) | # Duration # (s) | # Observation |
| # Tap switch position no. 3 (Principal) / Maximum peak on V limb |  |  |  |  |
| # CPRIBLRSCL25T1654 S002 | 16.80 | 7.53 | 0.54 | No abnormality |
| # CPRIBLRSCL25T1654 S003 | # 16.82 | # 7.66 | # 0.54 | # No abnormality |
| # CPRIBLRSCL25T1654 S004 | # 16.74 | # 7.71 | # 0.54 | # No abnormality |
| # Tap switch position no. 1 (Highest) / Maximum peak on W limb |  |  |  |  |
| # CPRIBLRSCL25T1654 S005 | # 16.89 | # 7.52 | # 0.54 | # No abnormality |
| # CPRIBLRSCL25T1654 S006 | # 16.78 | # 7.54 | # 0.54 | # No abnormality |
| # CPRIBLRSCL25T1654 S007 | # 16.72 | # 7.53 | # 0.54 | # No abnormality |
| # Tap switch position no. 7 (Lowest) / Maximum peak on U limb |  |  |  |  |
| # CPRIBLRSCL25T1654 S008 | # 16.49 | # 7.63 | # 0.54 | # No abnormality |
| # CPRIBLRSCL25T1654 S009 | # 16.34 | # 7.44 | # 0.54 | # No abnormality |
| # CPRIBLRSCL25T1654 S010 | # 16.26 | # 7.45 | # 0.54 | # No abnormality |
| Thermal Ability to Withstand Short-Circuit [Sub-clause 4.1 of IS: 2026 (Part-5):2011] # Tap switch position no. 3 (Principal) |  |  |  |  |
| # CPRIBLRSCL25T1654 S011 | # --- | # 7.55 | # 2.01 | # No abnormality |

P. Naveenkumar

Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 |  |  | Date: 18-11-2025 |  |  |
| --- | --- | --- | --- | --- | --- |
| # Reactance values after transformer attains ambient temperature |  |  |  |  |  |
| # Tap switch position |  | # % X before SCW test | # % X after SCW test |  | # % change in X |
| # Principal (3) |  | # 4.299 | # 4.306 |  | # -0.163 |
| # Highest (1) |  | # 4.365 | # 4.369 |  | # -0.092 |
| # Lowest (7) |  | # 4.397 | # 4.406 |  | # -0.205 |
| Variation of reactance is within limits |  |  |  |  |  |
| # Negative value of % change in reactance indicates increase in the value & vice versa |  |  |  |  |  |

SCW – Short-Circuit Withstand

Physical Inspection:

Conductor, core & clamping	: No visible damage

Spacers / Support blocks	: Intact

Oil				: Clear

ROUTINE TESTS

OIL LEAKAGE TEST

| Test Procedure | Transformer with all fittings including bushings in position, Air pressure was applied through breather connecting pipe. |
| --- | --- |
| Atmospheric pressure | 91.0 kPa |
| Ambient temperature | 25.0 C |

| Head pressure calculated at base of the tank kPa (g) | Test Pressure at base of tank kPa (g) | Test duration (Hours) | Observations |
| --- | --- | --- | --- |
| 14.0 | 28.0 | 8 | No leakage at any point |

Pressure (ROUTINE Test)

Test Procedure	Transformer tank fixed with all fittings including bushings in position,

Air pressure applied through breather connecting pipe.

Atmospheric Pressure  91.0 kPa

Ambient temperature      25.0 
      
      C

| Air pressure above atmospheric pressure (kPa) | Duration (Minutes) | Observations |
| --- | --- | --- |
| 35.0 | 10 | No leakage and no permanent deformation |

P. Naveenkumar

Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

TYPE TEST

Temperature-rise test

Test method				Short-circuit

Test conditions

## Source

Phases			Three

Frequency (Hz)			50

## Sample

HV terminals				Connected to three phase source

LV terminals				Shorted through copper links of negligible resistance

Tap position				Lowest Tap

## Measured Losses

| ## No load loss at rated voltage and at rated frequency (W) | ## 383.26 |
| --- | --- |
| ## Load loss at rated current at 75 C at lowest tap (W) | ## 2239.94 |

Test Procedure:

Step 1 - Total loss (2623.20 W) is injected until a steady state of oil temperature rise is established

Step 2 - The rated current (14.58 A) is injected for one hour, immediately after step-1.

The values of hot resistance of HV and LV windings at the time of shutdown are given in graphs CPRIBLRSCL25T1654
      
      G01 & CPRIBLRSCL25T1654
      
      G02 respectively.

Ambient temperature: 22.9
       ºC

| Measured Points | Temperature-rise (C) | Guaranteed Limit declared by the manufacturer (C) | Limit as per the standard (C) | Observations |
| --- | --- | --- | --- | --- |
| Top oil | 26.1 | 35 | 35 | Within limits |
| HV winding | 39.7 | 40 | 40 | Within limits |
| LV winding | 34.3 | 40 | 40 | Within limits |

P. Naveenkumar

Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

Pressure (TYPE TEST)

Test Procedure	Transformer tank fixed with all fittings including bushings in position.

First air and then vacuum applied through breather connecting pipe.

Atmospheric Pressure	91.0 kPa

Ambient temperature          25.0
       C

Air Pressure test:

| Air pressure above atmospheric pressure (kPa) | Duration (Minutes) | Permanent deflection of flat plate after release of air pressure (mm) | Observations |
| --- | --- | --- | --- |
| 80.0 | 30 | 1.08 | Within limits |

Vacuum test:

| Vacuum in level of mm of Mercury | Duration (Minutes) | Permanent deflection of flat plate after release of vacuum (mm) | Observations |
| --- | --- | --- | --- |
| 760 | 30 | 2.87 | Within limits |

# SPECIAL TESTS

No load current at 112.5 percent voltage

| Test Procedure | No-load current of transformer was measured at rated voltage and 112.5 % rated voltage at 50 Hz on LV side. Values are given below. |
| --- | --- |

| Average no-load current (Percentage of rated full load current) |  |  |  |
| --- | --- | --- | --- |
| At 100 percent rated voltage ( 433 V) |  | At 112.5 percent rated voltage (487 V) |  |
| Permissible value given in the standard | Measured value | Permissible value given in the standard | Measured value |
| 2 % | 0.51 % | 5 % | 1.28 % |

Conclusion: The sample tested complies with the requirement(s) of Clause(s) referred of IS 1180 (Part 1) :     2014 (with Amendment No.4: March 2021) for the tests conducted.

P. Naveenkumar

Test Engineer

TEST REPORT

| Test Report Number: CPRIBLRSCL25T1654 | Date: 18-11-2025 |
| --- | --- |

NOTE

- The Test results relate only to the sample(s) tested.

- Publication or reproduction of this Test Report in any form other than by complete set of the whole Test Report and in the language written is not permitted without the written consent of CPRI.

- Any Corrections / erasure invalidate the Test Report.

- Any anomaly / discrepancy in the Test Report should be brought to notice of CPRI within 45 days from the date of issue.

- All documents constituting the Test Report are stitched together with a continuous silk thread, the two ends of which have been brought over the front sheet of the Test Report and sealed with a CPRI logo printed paper sticker

- NABL has Accredited this laboratory as per ISO/IEC 17025-2017 vide Report no.TC-5452 for the tests carried out.

TC-5452

(P. Naveenkumar)

Test Engineer

--------------------------------------------------------End of Test Report--------------------------------------------------------