## Logsheet
CENTRAL POWER RESEARCH INSTITUTE - SHORT CIRCUIT LABORATORY, BENGALURU
LOG SHEET FOR TEMPERATURE-RISE TEST ON OIL IMMERSED / DRY TYPE TRANSFORMERS
Type your readings over the yellow {{placeholders}}. Blue cells are pre-filled by ATRG. Do not rename sheets' defined names. Station: Temperature Rise
Header
Test series no.
CPRI sample code
Customer / Manufacturer | M/s. A.P. Transformers, Chennai
Rating | 250 kVA, 11000/433 V, 3-phase
Serial no. | 1098
Date of test | 09-11-2025
Test details
Connections (HV / LV) | HV to 3-ph source, LV shorted
Tap position for TR test | LT (7)
Total losses applied (W) | 2623.2
No-load loss (NLL) (W) | 383.26
Full load loss at 75 °C (FLL) (W) | 2239.94
Rated current at selected tap (A) | 14.58
Readings during temperature rise test
Unit: W, °C | Time | Applied losses | Top oil | Bottom oil | Amb 1 | Amb 2 | Amb 3 | Amb 4 | Avg amb | Top-oil rise
0 | 09:40 | 2622.2 | 23.1 | 21.65 | 21.1 | 21 | 21.3
1 | 10:40 | 2622.2 | 29.8 | 23.85 | 20.8 | 20.85 | 21.15
2 | 11:40 | 2622.2 | 34.55 | 26 | 20.65 | 20.45 | 21.05
3 | 12:40 | 2622.2 | 38.8 | 28.55 | 20.45 | 20.35 | 20.85
4 | 13:40 | 2622.2 | 41.55 | 30.5 | 20.35 | 20.05 | 20.75
5 | 14:40 | 2622.2 | 43.45 | 31.8 | 20.35 | 20 | 20.75
6 | 15:40 | 2622.2 | 44 | 32.2 | 20.2 | 19.8 | 20.6
7 | 16:40 | 2622.2 | 45.5 | 33 | 20.1 | 19.6 | 20.5
8 | 17:40 | 2622.2 | 46 | 33.6 | 20 | 19.5 | 20.4 |  | 19.96 | 26.04
9 | 18:40 | 2622.2 | 46.55 | 34.05 | 19.8 | 19.35 | 20.3 |  | 19.81 | 26.74
10 | 19:40 | 2622.2 | 46.9 | 35.5 | 20.1 | 19.75 | 20.45 |  | 20.1 | 26.8
11 | 20:40 | 2622.2 | 47.95 | 36.65 | 21.1 | 20.8 | 21.1 |  | 21 | 26.95
12 | 21:30 | 2622.2 | 49 | 37.9 | 22.85 | 22.85 | 22.85 |  | 22.85 | 26.15
13
14
15
16
Winding resistance - cold and hot
HV cold resistance (Ω) | 3.554
LV cold resistance (mΩ) | 3.8844
Ambient during cold resistance measurement (°C) | 25.9
HV hot resistance at shutdown (Ω) | 4.0464
LV hot resistance at shutdown (mΩ) | 4.3425
Average ambient at shutdown (°C) | 22.85
Correction factor HV (°C) | 0.475
Correction factor LV (°C) | 0.475
Results (as calculated on logsheet)
Top-oil temperature rise (°C) | 26.1
HV winding temperature rise (°C) | 39.7
LV winding temperature rise (°C) | 34.3
Customer's Signature | [6 empty] | Test Engineer
DOCUMENT : FORMS & FORMATS - generated by CPRI ATRG